## Checklist Details
Title | Details
Checklist name | LT_Mini_Pillar
Category | LT
Subcategory | Mini Pillar
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 02:40 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 02:40 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:19 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10461550
Basic Details | Vendor Name | Kirloskar Electric Company Ltd.
Basic Details | Offered Qty | 75 Nos
Basic Details | PO Details | PO No. 4500134567 dated 01-Jul-2026
Basic Details | AEML Engineer & Designation | Rajesh Sharma, Senior Engineer (QA)
Basic Details | Vendor Engineer & Designation | Suresh Iyer, Production In-charge
Basic Details | Sl Nos of Items | LTMP/2026/0601 to LTMP/2026/0675
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Visual & Physical Checks | Dimensions | Ok
Visual & Physical Checks | Sheet Steel Thickness & Type | Canopy -3mm¦Others 2mm- OK
Visual & Physical Checks | Electrical Clearances | Ok
Visual & Physical Checks | Earthing | Ok
Visual & Physical Checks | Paint Shade & Thickness | Ok
Visual & Physical Checks | Gland Plate- Hole Size and Knockouts | Ok
Visual & Physical Checks | Hardware | Ok |  | SS hardware complete as per BOM packing list.
Visual & Physical Checks | Door Hinges /Interlock for door removal from hinge | Ok
Visual & Physical Checks | Locking Arrangement | Ok
Visual & Physical Checks | Danger Boards | Ok |  | Legend and fixing checked — OK.
Visual & Physical Checks | Foundation Structure | Ok
BOM Verification | Bill of Material | Ok |  | No BOM deviation vs approved revision.
Fabrication & Manufacturing Quality Checks | Welding | Ok |  | Fillet welds visually OK; no undercut on sample check.
Fabrication & Manufacturing Quality Checks | Finishing & Painting | Ok |  | Surface finish uniform; no runs or bare patches.
Raw Material / Bought out Items TC Verification | TC of GI sheet from raw material sub vendor | Ok
Raw Material / Bought out Items TC Verification | Bus Bar Conductivity | Ok |  | Conductivity within specified % IACS — OK.
Photos Upload | All 4 sides view with door closed condition | Attached
Photos Upload | Door Open Views Front & Back | Attached
Photos Upload | Foundation Structure View | Attached
Acceptance Tests as per QAP/IS | Insulation resistance test phase to phase & phase to earth | Ok |  | IR > 100 MΩ @ 500 V DC all combinations — Pass.
Acceptance Tests as per QAP/IS | High voltage test | Ok
Acceptance Tests as per QAP/IS | Powder coating thickness measurement | Ok
Acceptance Tests as per QAP/IS | Al Bus Bar conductivity measurement | Ok
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Ok |  | No unsafe condition noted during walk-through.
Other Compliances for Manufacturing Facility | House Keeping | Ok |  | Housekeeping satisfactory for inspection area.
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Ok
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Ok

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | Powder coating thickness at corners measured 60–70 microns (spec min 60); accepted.
Default | 2 | Calibration certificates of megger and coating thickness gauge verified valid till next due date.
Default | 3 | All offered serials verified against packing list; no short supply.

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Ok
Inspection Summary | Technical Clearance | Subject to rectification of minor defects
Inspection Summary | Declaration | Visual, dimensional and electrical acceptance tests carried out as per IS and AEML QAP. Lot cleared for dispatch.