## Checklist Details
Title | Details
Checklist name | LT_Mini_Pillar
Category | LT
Subcategory | Mini Pillar
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 01:23 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 01:23 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:19 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10460112
Basic Details | Vendor Name | Larsen & Toubro Ltd. (Electrical & Automation)
Basic Details | Offered Qty | 25 Nos
Basic Details | PO Details | PO No. 4500134567 dated 01-Jul-2026
Basic Details | AEML Engineer & Designation | Rajesh Sharma, Senior Engineer (QA)
Basic Details | Vendor Engineer & Designation | Amit Verma, Quality Engineer
Basic Details | Sl Nos of Items | LTMP/2026/0601 to LTMP/2026/0675
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Visual & Physical Checks | Dimensions | Ok
Visual & Physical Checks | Sheet Steel Thickness & Type | Others 2mm- OK
Visual & Physical Checks | Electrical Clearances | Ok |  | Clearance verified with feeler gauge — OK.
Visual & Physical Checks | Earthing | Ok |  | Earth continuity checked; resistance within limit.
Visual & Physical Checks | Paint Shade & Thickness | Ok |  | Shade RAL as approved; DFT 60–75 microns average.
Visual & Physical Checks | Gland Plate- Hole Size and Knockouts | Ok
Visual & Physical Checks | Hardware | Ok
Visual & Physical Checks | Door Hinges /Interlock for door removal from hinge | Ok
Visual & Physical Checks | Locking Arrangement | Ok
Visual & Physical Checks | Danger Boards | Ok |  | Danger board fixed with rivets / screws as per drawing.
Visual & Physical Checks | Foundation Structure | Ok |  | Foundation bolt pitch matches civil drawing.
BOM Verification | Bill of Material | Ok
Fabrication & Manufacturing Quality Checks | Welding | Ok
Fabrication & Manufacturing Quality Checks | Finishing & Painting | Ok
Raw Material / Bought out Items TC Verification | TC of GI sheet from raw material sub vendor | Ok
Raw Material / Bought out Items TC Verification | Bus Bar Conductivity | Ok
Photos Upload | All 4 sides view with door closed condition | Attached
Photos Upload | Door Open Views Front & Back | Attached
Photos Upload | Foundation Structure View | Attached
Acceptance Tests as per QAP/IS | Insulation resistance test phase to phase & phase to earth | Ok
Acceptance Tests as per QAP/IS | High voltage test | Ok
Acceptance Tests as per QAP/IS | Powder coating thickness measurement | Ok
Acceptance Tests as per QAP/IS | Al Bus Bar conductivity measurement | Ok |  | Measured conductivity within limit; values logged.
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Ok
Other Compliances for Manufacturing Facility | House Keeping | Ok |  | Housekeeping satisfactory for inspection area.
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Ok
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Ok |  | SA 8000 certificate displayed; validity checked.

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | All dimensional, electrical clearance and earthing checks conform to the approved GA drawing and applicable IS standards.
Default | 2 | Sheet steel thickness, paint shade, powder coating thickness and BOM are as per the approved specification; no deviation observed.
Default | 3 | Acceptance tests (insulation resistance, high voltage, bus bar conductivity) completed satisfactorily; material is recommended for dispatch clearance.

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Ok
Inspection Summary | Technical Clearance | Yes |  | Clearance recommended subject to packing confirmation.
Inspection Summary | Declaration | Visual, dimensional and electrical acceptance tests carried out as per IS and AEML QAP. Lot cleared for dispatch.