## Checklist Details
Title | Details
Checklist name | LT_Mini_Pillar
Category | LT
Subcategory | Mini Pillar
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 12:52 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 12:52 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:19 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10461550
Basic Details | Vendor Name | ABB India Limited
Basic Details | Offered Qty | 50 Nos
Basic Details | PO Details | PO No. 4500137890 dated 20-Jul-2026
Basic Details | AEML Engineer & Designation | Rajesh Sharma, Senior Engineer (QA)
Basic Details | Vendor Engineer & Designation | Suresh Iyer, Production In-charge
Basic Details | Sl Nos of Items | LTMP/2026/0501 to LTMP/2026/0525
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Visual & Physical Checks | Dimensions | Ok |  | Overall H×W×D verified on 3 samples — OK.
Visual & Physical Checks | Sheet Steel Thickness & Type | Canopy -3mm |  | Body sheet below 2 mm at side panel — Not OK.
Visual & Physical Checks | Electrical Clearances | Ok
Visual & Physical Checks | Earthing | Ok
Visual & Physical Checks | Paint Shade & Thickness | Ok
Visual & Physical Checks | Gland Plate- Hole Size and Knockouts | Ok
Visual & Physical Checks | Hardware | Ok
Visual & Physical Checks | Door Hinges /Interlock for door removal from hinge | Not Ok
Visual & Physical Checks | Locking Arrangement | Ok
Visual & Physical Checks | Danger Boards | Not Ok |  | Danger board loose on two units; re-fixed during visit.
Visual & Physical Checks | Foundation Structure | Not Ok |  | Bolt hole pitch off by ~5 mm — civil mismatch.
BOM Verification | Bill of Material | Not Ok |  | No BOM deviation vs approved revision.
Fabrication & Manufacturing Quality Checks | Welding | Not Ok
Fabrication & Manufacturing Quality Checks | Finishing & Painting | Not Ok
Raw Material / Bought out Items TC Verification | TC of GI sheet from raw material sub vendor | Not Ok
Raw Material / Bought out Items TC Verification | Bus Bar Conductivity | Not Ok
Photos Upload | All 4 sides view with door closed condition | Not Attached
Photos Upload | Door Open Views Front & Back | Attached
Photos Upload | Foundation Structure View | Attached
Acceptance Tests as per QAP/IS | Insulation resistance test phase to phase & phase to earth | Ok
Acceptance Tests as per QAP/IS | High voltage test | Ok |  | Passed as per QAP acceptance criteria.
Acceptance Tests as per QAP/IS | Powder coating thickness measurement | Not Ok
Acceptance Tests as per QAP/IS | Al Bus Bar conductivity measurement | Not Ok |  | Measured value outside acceptance band.
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Ok |  | No unsafe condition noted during walk-through.
Other Compliances for Manufacturing Facility | House Keeping | Not Ok |  | Oil spills near packing bay; slip hazard noted.
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Not Ok
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Not Ok

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | Gland plate knockout sizes verified against cable schedule; one spare knockout to be blanked before dispatch.
Default | 2 | Danger board fixing found loose on two units; re-fixed with spring washers and verified.
Default | 3 | Foundation bolt hole pitch matches approved civil drawing; no rework required.

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Not Ok
Inspection Summary | Technical Clearance | Yes
Inspection Summary | Declaration | Re-inspection will be required after rectification of the non-conformances listed in observations. Present lot is not cleared for dispatch.