## Checklist Details
Title | Details
Checklist name | LT_Mini_Pillar
Category | LT
Subcategory | Mini Pillar
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 12:32 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 12:32 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:19 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10460112
Basic Details | Vendor Name | Siemens Ltd. – Smart Infrastructure
Basic Details | Offered Qty | 40 Nos
Basic Details | PO Details | PO No. 4500128910 dated 02-Jun-2026
Basic Details | AEML Engineer & Designation | Sandeep Patil, Dy. Manager (Quality)
Basic Details | Vendor Engineer & Designation | Suresh Iyer, Production In-charge
Basic Details | Sl Nos of Items | AEML-MP-2607-001 to AEML-MP-2607-040
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Visual & Physical Checks | Dimensions | Ok
Visual & Physical Checks | Sheet Steel Thickness & Type | Not OK
Visual & Physical Checks | Electrical Clearances | Not Ok |  | Phase–phase and phase–earth clearances as per IS / GA.
Visual & Physical Checks | Earthing | Not Ok
Visual & Physical Checks | Paint Shade & Thickness | Ok |  | Shade RAL as approved; DFT 60–75 microns average.
Visual & Physical Checks | Gland Plate- Hole Size and Knockouts | Ok |  | Knockouts match cable schedule; unused blanks fitted.
Visual & Physical Checks | Hardware | Ok |  | SS hardware complete as per BOM packing list.
Visual & Physical Checks | Door Hinges /Interlock for door removal from hinge | Not Ok
Visual & Physical Checks | Locking Arrangement | Not Ok
Visual & Physical Checks | Danger Boards | Ok |  | Board missing on Sl. LTMP/2026/0470.
Visual & Physical Checks | Foundation Structure | Ok |  | Base channel twist noted; needs correction.
BOM Verification | Bill of Material | Not Ok
Fabrication & Manufacturing Quality Checks | Welding | Not Ok
Fabrication & Manufacturing Quality Checks | Finishing & Painting | Not Ok
Raw Material / Bought out Items TC Verification | TC of GI sheet from raw material sub vendor | Ok
Raw Material / Bought out Items TC Verification | Bus Bar Conductivity | Ok |  | Mill TC missing for offered bus bar lot.
Photos Upload | All 4 sides view with door closed condition | Not Attached
Photos Upload | Door Open Views Front & Back | Attached
Photos Upload | Foundation Structure View | Not Attached
Acceptance Tests as per QAP/IS | Insulation resistance test phase to phase & phase to earth | Not Ok |  | IR phase–earth below acceptance on one sample.
Acceptance Tests as per QAP/IS | High voltage test | Ok
Acceptance Tests as per QAP/IS | Powder coating thickness measurement | Ok
Acceptance Tests as per QAP/IS | Al Bus Bar conductivity measurement | Ok
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Not Ok
Other Compliances for Manufacturing Facility | House Keeping | Not Ok
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Ok
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Ok |  | Evidence of compliance not produced on request.

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | Minor paint shade variation observed on rear canopy; vendor advised to touch up before packing.
Default | 2 | Door hinge interlock operation found stiff on one sample; adjusted on shop floor and rechecked OK.
Default | 3 | IR values phase-to-earth measured above 100 MΩ; HV test passed at specified voltage for 1 minute.

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Not Ok
Inspection Summary | Technical Clearance | Yes
Inspection Summary | Declaration | Inspection completed jointly with the vendor QA team. All critical parameters verified against approved drawings and QAP; unit is recommended for dispatch.