## Checklist Details
Title | Details
Checklist name | LT_Mini_Pillar
Category | LT
Subcategory | Mini Pillar
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 02:42 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 02:42 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:19 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10460112
Basic Details | Vendor Name | ABB India Limited
Basic Details | Offered Qty | 50 Nos
Basic Details | PO Details | PO No. 4500137890 dated 20-Jul-2026
Basic Details | AEML Engineer & Designation | Rajesh Sharma, Senior Engineer (QA)
Basic Details | Vendor Engineer & Designation | Amit Verma, Quality Engineer
Basic Details | Sl Nos of Items | LTMP/2026/0501 to LTMP/2026/0525
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Visual & Physical Checks | Dimensions | Not Ok
Visual & Physical Checks | Sheet Steel Thickness & Type | Canopy -3mm¦Not OK |  | Canopy measured 2.6 mm at front edge (spec 3 mm).
Visual & Physical Checks | Electrical Clearances | Not Ok |  | Phase–earth clearance short near bus support insulator.
Visual & Physical Checks | Earthing | Not Ok
Visual & Physical Checks | Paint Shade & Thickness | Not Ok
Visual & Physical Checks | Gland Plate- Hole Size and Knockouts | Not Ok
Visual & Physical Checks | Hardware | Not Ok
Visual & Physical Checks | Door Hinges /Interlock for door removal from hinge | Not Ok |  | Interlock stiff / jammed on sample; adjusted pending recheck.
Visual & Physical Checks | Locking Arrangement | Not Ok
Visual & Physical Checks | Danger Boards | Not Ok
Visual & Physical Checks | Foundation Structure | Not Ok
BOM Verification | Bill of Material | Not Ok |  | Bus support insulator qty short vs BOM.
Fabrication & Manufacturing Quality Checks | Welding | Not Ok
Fabrication & Manufacturing Quality Checks | Finishing & Painting | Not Ok
Raw Material / Bought out Items TC Verification | TC of GI sheet from raw material sub vendor | Not Ok |  | Sub-vendor TC expired / not available for offered lot.
Raw Material / Bought out Items TC Verification | Bus Bar Conductivity | Not Ok
Photos Upload | All 4 sides view with door closed condition | Not Attached
Photos Upload | Door Open Views Front & Back | Not Attached
Photos Upload | Foundation Structure View | Not Attached
Acceptance Tests as per QAP/IS | Insulation resistance test phase to phase & phase to earth | Not Ok
Acceptance Tests as per QAP/IS | High voltage test | Not Ok
Acceptance Tests as per QAP/IS | Powder coating thickness measurement | Not Ok
Acceptance Tests as per QAP/IS | Al Bus Bar conductivity measurement | Not Ok
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Not Ok |  | Welding without screen in open bay — safety observation.
Other Compliances for Manufacturing Facility | House Keeping | Not Ok |  | Scrap mixed with finished goods staging — improve HK.
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Not Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Not Ok |  | DFT gauge calibration overdue by 15 days.
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Not Ok

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | Welding undercut at bottom channel joint; dye-penetrant check failed — repair pending.
Default | 2 | Danger board missing / loosely fixed on multiple units; safety non-conformance.
Default | 3 | Bus bar conductivity out of specified limit on sample; TC mismatch under review.

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Not Ok |  | Lot not meeting QAP acceptance criteria.
Inspection Summary | Technical Clearance | Rejected
Inspection Summary | Declaration | Acceptance tests / visual checks not meeting specification. Material is rejected for the offered lot.