## Checklist Details
Title | Details
Checklist name | LT_Power_Cables
Category | LT
Subcategory | Power Cables
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 02:43 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 02:43 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:13 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10571550
Basic Details | Cable Size | 1C x 630 sq.mm Al, XLPE, Unarmoured
Basic Details | Vendor Name | Polycab India Ltd.
Basic Details | Offered Qty | 10 Drums / 5000 mtr
Basic Details | PO Details | PO No. 4500156789 dated 05-Jul-2026
Basic Details | Batch Nos | FX/ARM/260630/21 to FX/ARM/260630/28
Basic Details | AEML Engineer & Designation | Priya Nair, Executive Engineer (Inspection)
Basic Details | Vendor Engineer & Designation | Ramesh Pillai, Works Manager
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Physical Checks | Overall Cable Dia | 41.8 mm (as per GA / QAP) |  | Diameter check with digital Vernier – conforms to approved construction.
Physical Checks | Ovality of Cable | 1.2% (max allowed 2%) – OK |  | Ovality calculated from max–min OD; within 2% limit.
Physical Checks | Outer Sheath Thickness | Avg 3.10 mm, Min 2.90 mm – OK
Physical Checks | Water Swellable Tape thickness | 0.22 mm (min 0.20 mm) – OK
Physical Checks | Armour Strand Size | 1.6 mm x 4.0 mm GI strip
Physical Checks | No of Armour Strands | 44 Nos
Physical Checks | Diameter over Armour | 45.0 mm
Physical Checks | Diameter over Inner Sheath | 35.8 mm
Physical Checks | Thickness of Inner Sheath | 1.25 mm – OK
Physical Checks | Diameter over laid up | 34.5 mm – OK
Physical Checks | Insulation Thickness | Avg 1.80 mm, Min 1.60 mm (spec min 1.60 mm)
Physical Checks | No of Strands in conductor | 37 strands – compact circular
Physical Checks | shape of conductor | Non-compacted circular
Physical Checks | Filler Diameter | 6.0 mm PP yarn / filler
Physical Checks | Verification of Water Blocking construction in conductor | Water blocking missing in mid strand layer – deviation / NCR |  | Construction does not match approved water-block design.
Acceptance Tests | Conductor Resistance Tests | R, Y, B phases within 2% – Pass
Acceptance Tests | High Voltage test @3kV for 5 minutes in all cores | Passed – no breakdown / flashover
Acceptance Tests | IR Test | IR phase–earth 80 MΩ – below acceptance; retest pending
Acceptance Tests | Hot Set Test on Insulation | Results within specified max – Pass
Acceptance Tests | Tensile Strength and Elongation for Insulation & Sheath | Sheath elongation after ageing below min – fail
Acceptance Tests | Water Swellable Tape Swell height | 7.5 mm swell – within limit – Pass
Acceptance Tests | Armour Tests - Mass of Zinc Coating & Uniformity of Zinc coating | Pass – TC from armour sub-vendor reviewed |  | Armour sub-vendor TC reviewed – Pass.
Acceptance Tests | Tests on HDPE Outer Sheath -1. Density 2.Thickness 3. Shrinkage 4. Pressure test at high temperature 5. Tensile Strength Without ageing & After ageing 6. Elongation at break 7. Without ageing & After ageing | All listed HDPE sheath tests satisfactory – Pass
Acceptance Tests | Water Penetration Test | No water penetration beyond sealed length – Pass
Acceptance Tests | Anti Termite & Anti Rodent check | Additive present as declared; marking OK – Pass |  | Additive declared; marking on sheath verified.
Acceptance Tests | FRLS Outer Sheath -Flammability Test | FRLS flammability OK – Pass
Acceptance Tests | FRLS Outer Sheath-Oxygen Index Test | OI 33% – Pass
Acceptance Tests | FRLS Outer Sheath -Temperature Index | TI within specified min – Pass |  | Temperature index within specified min.
Acceptance Tests | FRLS Outersheath -Halogen Gas Acid Evaluation | Pass – low halogen as required
Acceptance Tests | FRLS Outer Sheath-Smoke Density | Max smoke density < specified – Pass |  | Smoke density rating within max – Pass.
Cable Rewinding on Drum | Cable Appearances / Damages check | Appearance OK throughout offered length
Cable Rewinding on Drum | Outer sheath colour | Black outer sheath – OK
Cable Rewinding on Drum | Printing & Embossing | Legend as per AEML / PO requirement – OK
Cable Rewinding on Drum | Sequential Length Marking | Sequential marking every metre – verified OK |  | Metre marks continuous; start/end verified.
Cable Rewinding on Drum | MS Plates & Spinndle | End plates & spindle secure – OK
Cable Rewinding on Drum | Weight of Cable | 1980 kg verified on weighbridge – OK
Cable Rewinding on Drum | Drum Length Verification | 1000 mtr – OK |  | Drum length verified OK.
Packing & Marking | Cable End Sealing | OK
Packing & Marking | Drum Stencilling & Marking | OK
Inprocess Record Verification | Wire Drawing | Wire drawing QC sheets reviewed – OK
Inprocess Record Verification | Core Insulation | Ok
Inprocess Record Verification | Core Laying | In-process sheet OK
Inprocess Record Verification | Inner Sheathing | Verified – OK
Inprocess Record Verification | Armouring | Strand count & coverage logged – OK
Inprocess Record Verification | Outersheathing | Outer sheath extrusion records OK
Raw Material / Bought out Items TC Verification | Al Wire Rod | Ok |  | Conductivity / composition within limit – OK.
Raw Material / Bought out Items TC Verification | PVC Compound | Not Ok
Raw Material / Bought out Items TC Verification | HDPE Compound | Manufacturer TC reviewed – OK
Raw Material / Bought out Items TC Verification | Armour GI | GI armour TC verified – Zn coating OK
Raw Material / Bought out Items TC Verification | Water Swellable Tape / Yard | Water swellable tape TC OK
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Ok |  | No unsafe condition during walk-through.
Other Compliances for Manufacturing Facility | House Keeping | Not Ok
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Ok |  | Megger / HV / gauge cal certificates valid.
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Ok

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | Major |  | Severity elevated; lot disposition pending.
Default | 2 | Critical |  | Requires vendor CAPA and re-inspection.

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Not Ok
Inspection Summary | Technical Clearance | Yes
Inspection Summary | Declaration | Re-inspection will be required after rectification of non-conformances. Present lot is not cleared for dispatch.