## Checklist Details
Title | Details
Checklist name | LT_Power_Cables
Category | LT
Subcategory | Power Cables
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 02:41 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 02:41 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:13 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10567201
Basic Details | Cable Size | 3C x 400 sq.mm Al, XLPE, Armoured
Basic Details | Vendor Name | KEI Industries Ltd.
Basic Details | Offered Qty | 6 Drums / 3000 mtr
Basic Details | PO Details | PO No. 4500145678 dated 10-May-2026
Basic Details | Batch Nos | KEI/AL/XLPE/2606/112 to KEI/AL/XLPE/2606/119
Basic Details | AEML Engineer & Designation | Vikram Desai, Manager (Vendor Quality)
Basic Details | Vendor Engineer & Designation | Amit Verma, Quality Engineer
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Physical Checks | Overall Cable Dia | 48.5 mm (spec 47.0 – 50.0 mm) |  | Diameter check with digital Vernier – conforms to approved construction.
Physical Checks | Ovality of Cable | 2.0% – at limit, accepted
Physical Checks | Outer Sheath Thickness | Avg 2.65 mm, Min 2.50 mm – OK
Physical Checks | Water Swellable Tape thickness | 0.25 mm both longitudinal & overlapping – OK |  | Tape thickness matches BOM; overlap verified.
Physical Checks | Armour Strand Size | 2.5 mm GI round wire – OK
Physical Checks | No of Armour Strands | 56 Nos
Physical Checks | Diameter over Armour | 47.2 mm
Physical Checks | Diameter over Inner Sheath | 42.0 mm
Physical Checks | Thickness of Inner Sheath | 1.25 mm – OK
Physical Checks | Diameter over laid up | 39.0 mm
Physical Checks | Insulation Thickness | Avg 1.80 mm, Min 1.60 mm (spec min 1.60 mm)
Physical Checks | No of Strands in conductor | 61 strands of 2.52 mm dia
Physical Checks | shape of conductor | Compacted circular – OK
Physical Checks | Filler Diameter | 4.0 mm – OK
Physical Checks | Verification of Water Blocking construction in conductor | Verified – matches QAP / type test construction
Acceptance Tests | Conductor Resistance Tests | 0.118 Ω/km @ 20°C – above max; conductor resistance fail |  | Conductor resistance fail – investigate strand / alloy.
Acceptance Tests | High Voltage test @3kV for 5 minutes in all cores | Passed as per QAP |  | HV kit cal valid; test witnessed – Pass.
Acceptance Tests | IR Test | IR phase–earth 80 MΩ – below acceptance; retest pending
Acceptance Tests | Hot Set Test on Insulation | Elongation under load 45%, permanent set 8% – Pass
Acceptance Tests | Tensile Strength and Elongation for Insulation & Sheath | Values within IS limits before & after ageing – Pass
Acceptance Tests | Water Swellable Tape Swell height | Swell test OK – Pass
Acceptance Tests | Armour Tests - Mass of Zinc Coating & Uniformity of Zinc coating | Zn coating mass & uniformity within IS 3975 – Pass
Acceptance Tests | Tests on HDPE Outer Sheath -1. Density 2.Thickness 3. Shrinkage 4. Pressure test at high temperature 5. Tensile Strength Without ageing & After ageing 6. Elongation at break 7. Without ageing & After ageing | All listed HDPE sheath tests satisfactory – Pass |  | Density / shrinkage / pressure / TS–E – Pass.
Acceptance Tests | Water Penetration Test | Longitudinal WP test satisfactory – Pass |  | WP test as per QAP – satisfactory.
Acceptance Tests | Anti Termite & Anti Rodent check | Additive present as declared; marking OK – Pass
Acceptance Tests | FRLS Outer Sheath -Flammability Test | Flame propagated beyond mark – flammability fail
Acceptance Tests | FRLS Outer Sheath-Oxygen Index Test | OI 31.5% – Pass
Acceptance Tests | FRLS Outer Sheath -Temperature Index | Pass
Acceptance Tests | FRLS Outersheath -Halogen Gas Acid Evaluation | Halogen acid above limit – fail |  | HCl evaluation does not meet FRLS criteria.
Acceptance Tests | FRLS Outer Sheath-Smoke Density | Max smoke density < specified – Pass |  | FRLS smoke density OK per lab sheet.
Cable Rewinding on Drum | Cable Appearances / Damages check | Minor scuff mark cleaned; no deep cut – OK |  | Surface finish satisfactory over offered length.
Cable Rewinding on Drum | Outer sheath colour | Black outer sheath – OK
Cable Rewinding on Drum | Printing & Embossing | Printing clear: size, voltage grade, IS mark, manufacturer, year – OK
Cable Rewinding on Drum | Sequential Length Marking | Verified start & end metre marks – OK
Cable Rewinding on Drum | MS Plates & Spinndle | MS plates painted / marked – OK
Cable Rewinding on Drum | Weight of Cable | 2100 kg gross – OK
Cable Rewinding on Drum | Drum Length Verification | 250 mtr – verified
Packing & Marking | Cable End Sealing | Proper end caps fitted – OK
Packing & Marking | Drum Stencilling & Marking | Drum no. & arrow marking OK
Inprocess Record Verification | Wire Drawing | Wire drawing QC sheets reviewed – OK
Inprocess Record Verification | Core Insulation | Ok |  | Thickness & spark test logs complete.
Inprocess Record Verification | Core Laying | Core laying & filler arrangement as per drawing – OK
Inprocess Record Verification | Inner Sheathing | Thickness logged – within limit – OK
Inprocess Record Verification | Armouring | Verified – OK
Inprocess Record Verification | Outersheathing | Outer sheath extrusion records OK
Raw Material / Bought out Items TC Verification | Al Wire Rod | Ok
Raw Material / Bought out Items TC Verification | PVC Compound | Ok
Raw Material / Bought out Items TC Verification | HDPE Compound | Verified – OK
Raw Material / Bought out Items TC Verification | Armour GI | Sub-vendor TC reviewed – OK
Raw Material / Bought out Items TC Verification | Water Swellable Tape / Yard | TC verified – swell properties OK
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Ok |  | PPE & emergency preparedness observed OK.
Other Compliances for Manufacturing Facility | House Keeping | Ok
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Ok
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Ok |  | No adverse social-compliance observation.

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | Minor
Default | 2 | Minor |  | No blocking issue on observation point 2.

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Not Ok
Inspection Summary | Technical Clearance | Subject to rectification of minor defects |  | Clearance withheld – re-inspection / rejection.
Inspection Summary | Declaration | Re-inspection will be required after rectification of non-conformances. Present lot is not cleared for dispatch.