## Checklist Details
Title | Details
Checklist name | LT_Power_Cables
Category | LT
Subcategory | Power Cables
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 01:12 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 01:12 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:13 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10568934
Basic Details | Cable Size | 3.5C x 240 sq.mm Al, XLPE, Armoured
Basic Details | Vendor Name | Finolex Cables Ltd.
Basic Details | Offered Qty | 10 Drums / 5000 mtr
Basic Details | PO Details | PO No. 4500160123 dated 18-Jul-2026
Basic Details | Batch Nos | PC/LT/2607/A01 to PC/LT/2607/A05
Basic Details | AEML Engineer & Designation | Vikram Desai, Manager (Vendor Quality)
Basic Details | Vendor Engineer & Designation | Amit Verma, Quality Engineer
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Physical Checks | Overall Cable Dia | 52.2 mm (within approved drawing tolerance)
Physical Checks | Ovality of Cable | 1.2% (max allowed 2%) – OK
Physical Checks | Outer Sheath Thickness | Min thickness 2.20 mm – below spec min; rework / hold
Physical Checks | Water Swellable Tape thickness | 0.15 mm – below min; tape construction incomplete
Physical Checks | Armour Strand Size | 1.6 mm x 4.0 mm GI strip
Physical Checks | No of Armour Strands | 56 Nos
Physical Checks | Diameter over Armour | 42.5 mm
Physical Checks | Diameter over Inner Sheath | 38.2 mm
Physical Checks | Thickness of Inner Sheath | 1.15 mm average – conforms
Physical Checks | Diameter over laid up | 39.0 mm
Physical Checks | Insulation Thickness | Avg 1.90 mm, Min 1.70 mm – OK
Physical Checks | No of Strands in conductor | 53 strands – as per schedule
Physical Checks | shape of conductor | Compacted circular – OK
Physical Checks | Filler Diameter | 4.0 mm – OK
Physical Checks | Verification of Water Blocking construction in conductor | Water blocking missing in mid strand layer – deviation / NCR
Acceptance Tests | Conductor Resistance Tests | R, Y, B phases within 2% – Pass
Acceptance Tests | High Voltage test @3kV for 5 minutes in all cores | Passed – no breakdown / flashover |  | Flashover during withstand – lot on hold.
Acceptance Tests | IR Test | >2000 MΩ measured – Pass |  | Megger readings stable after 1 min – Pass.
Acceptance Tests | Hot Set Test on Insulation | Permanent set 18% – out of limit; hot set fail |  | Insulation compound / cure issue suspected.
Acceptance Tests | Tensile Strength and Elongation for Insulation & Sheath | Insulation & sheath mechanical properties OK – Pass |  | Mechanical properties OK for XLPE / sheath.
Acceptance Tests | Water Swellable Tape Swell height | Swell height 3 mm – below requirement; fail
Acceptance Tests | Armour Tests - Mass of Zinc Coating & Uniformity of Zinc coating | Mass of zinc & Preece test OK – Pass
Acceptance Tests | Tests on HDPE Outer Sheath -1. Density 2.Thickness 3. Shrinkage 4. Pressure test at high temperature 5. Tensile Strength Without ageing & After ageing 6. Elongation at break 7. Without ageing & After ageing | Density, thickness, shrinkage, pressure, TS & elongation – all Pass
Acceptance Tests | Water Penetration Test | Water ingress observed beyond limit – WP test fail
Acceptance Tests | Anti Termite & Anti Rodent check | Additive present as declared; marking OK – Pass
Acceptance Tests | FRLS Outer Sheath -Flammability Test | Flammability test Pass as per IEC / IS |  | Flammability as per IEC / IS – OK.
Acceptance Tests | FRLS Outer Sheath-Oxygen Index Test | OI 27% – below min 30%; oxygen index fail
Acceptance Tests | FRLS Outer Sheath -Temperature Index | Pass – as per FRLS compound TC |  | Temperature index within specified min.
Acceptance Tests | FRLS Outersheath -Halogen Gas Acid Evaluation | Pass – low halogen as required |  | Halogen acid gas within FRLS limit.
Acceptance Tests | FRLS Outer Sheath-Smoke Density | Smoke density rating within limit – Pass |  | Smoke density rating within max – Pass.
Cable Rewinding on Drum | Cable Appearances / Damages check | Deep sheath cut / abrasion on outer layer – damage; rework pending
Cable Rewinding on Drum | Outer sheath colour | Black
Cable Rewinding on Drum | Printing & Embossing | Embossing / inkjet legible throughout – OK
Cable Rewinding on Drum | Sequential Length Marking | OK
Cable Rewinding on Drum | MS Plates & Spinndle | MS plates fitted; spindle hole OK – OK
Cable Rewinding on Drum | Weight of Cable | 1850 kg (drum + cable) – matches packing list
Cable Rewinding on Drum | Drum Length Verification | 1000 mtr – OK
Packing & Marking | Cable End Sealing | OK |  | End sealing intact before packing.
Packing & Marking | Drum Stencilling & Marking | Drum stencilled: size, length, voltage, PO, drum no., direction of rotation – OK
Inprocess Record Verification | Wire Drawing | Records complete for offered batch – OK
Inprocess Record Verification | Core Insulation | Ok
Inprocess Record Verification | Core Laying | OK
Inprocess Record Verification | Inner Sheathing | Thickness logged – within limit – OK
Inprocess Record Verification | Armouring | OK
Inprocess Record Verification | Outersheathing | OK
Raw Material / Bought out Items TC Verification | Al Wire Rod | Ok
Raw Material / Bought out Items TC Verification | PVC Compound | Ok |  | PVC compound TC reviewed – grade & batch OK.
Raw Material / Bought out Items TC Verification | HDPE Compound | TC verified – grade & batch match – OK
Raw Material / Bought out Items TC Verification | Armour GI | Sub-vendor TC reviewed – OK
Raw Material / Bought out Items TC Verification | Water Swellable Tape / Yard | OK
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Ok |  | PPE & emergency preparedness observed OK.
Other Compliances for Manufacturing Facility | House Keeping | Ok
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Not Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Not Ok
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Ok |  | SA 8000 certificate displayed; validity OK.

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | Minor
Default | 2 | Minor |  | Observation 2 closed / Minor only.

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Not Ok |  | One or more acceptance tests Not Ok.
Inspection Summary | Technical Clearance | Yes
Inspection Summary | Declaration | All critical electrical and construction parameters verified against approved specification. Lot is acceptable for release to site.