## Checklist Details
Title | Details
Checklist name | LT_Power_Cables
Category | LT
Subcategory | Power Cables
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 01:05 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 01:05 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:13 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10570112
Basic Details | Cable Size | 3.5C x 240 sq.mm Al, XLPE, Armoured
Basic Details | Vendor Name | Finolex Cables Ltd.
Basic Details | Offered Qty | 6 Drums / 3000 mtr
Basic Details | PO Details | PO No. 4500160123 dated 18-Jul-2026
Basic Details | Batch Nos | FX/ARM/260630/21 to FX/ARM/260630/28
Basic Details | AEML Engineer & Designation | Rajesh Sharma, Senior Engineer (QA)
Basic Details | Vendor Engineer & Designation | Neha Kulkarni, QA Supervisor
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Physical Checks | Overall Cable Dia | 52.2 mm (within approved drawing tolerance) |  | Diameter check with digital Vernier – conforms to approved construction.
Physical Checks | Ovality of Cable | 2.8% – above max 2%; ovality fail on sample |  | Ovality fail – possible sheath / armour lay issue.
Physical Checks | Outer Sheath Thickness | 2.75 mm average – conforms to IS
Physical Checks | Water Swellable Tape thickness | 0.30 mm – OK
Physical Checks | Armour Strand Size | 2.0 mm dia – matches approved drawing
Physical Checks | No of Armour Strands | 52 Nos
Physical Checks | Diameter over Armour | 47.2 mm
Physical Checks | Diameter over Inner Sheath | 37.5 mm – OK
Physical Checks | Thickness of Inner Sheath | Avg 1.30 mm, Min 1.10 mm – OK
Physical Checks | Diameter over laid up | 35.0 mm
Physical Checks | Insulation Thickness | 1.85 mm – conforms to IS 7098
Physical Checks | No of Strands in conductor | 53 strands – as per schedule
Physical Checks | shape of conductor | Compacted circular
Physical Checks | Filler Diameter | 4.0 mm – OK
Physical Checks | Verification of Water Blocking construction in conductor | Present and continuous along conductor – OK
Acceptance Tests | Conductor Resistance Tests | 0.118 Ω/km @ 20°C – above max; conductor resistance fail
Acceptance Tests | High Voltage test @3kV for 5 minutes in all cores | HV test completed satisfactorily – Pass
Acceptance Tests | IR Test | IR values satisfactory – Pass
Acceptance Tests | Hot Set Test on Insulation | Permanent set 18% – out of limit; hot set fail |  | Insulation compound / cure issue suspected.
Acceptance Tests | Tensile Strength and Elongation for Insulation & Sheath | Insulation TS 12.5 N/mm², E 200%; Sheath TS 12.0, E 250% – Pass
Acceptance Tests | Water Swellable Tape Swell height | 7.5 mm swell – within limit – Pass
Acceptance Tests | Armour Tests - Mass of Zinc Coating & Uniformity of Zinc coating | Zn mass 180 g/m² – below min; armour coating fail
Acceptance Tests | Tests on HDPE Outer Sheath -1. Density 2.Thickness 3. Shrinkage 4. Pressure test at high temperature 5. Tensile Strength Without ageing & After ageing 6. Elongation at break 7. Without ageing & After ageing | Pass – results as per attached lab sheet
Acceptance Tests | Water Penetration Test | No water penetration beyond sealed length – Pass
Acceptance Tests | Anti Termite & Anti Rodent check | Verified on outer sheath – Pass
Acceptance Tests | FRLS Outer Sheath -Flammability Test | Pass |  | Flammability as per IEC / IS – OK.
Acceptance Tests | FRLS Outer Sheath-Oxygen Index Test | Oxygen index 32% (min 30%) – Pass |  | OI ≥ 30% – Pass.
Acceptance Tests | FRLS Outer Sheath -Temperature Index | Temperature index 280°C – Pass
Acceptance Tests | FRLS Outersheath -Halogen Gas Acid Evaluation | Pass – lab result OK
Acceptance Tests | FRLS Outer Sheath-Smoke Density | Pass
Cable Rewinding on Drum | Cable Appearances / Damages check | No damage found during rewind – OK
Cable Rewinding on Drum | Outer sheath colour | Black with FRLS marking
Cable Rewinding on Drum | Printing & Embossing | OK – batch / drum ref printed
Cable Rewinding on Drum | Sequential Length Marking | Length marking accurate within tolerance – OK
Cable Rewinding on Drum | MS Plates & Spinndle | OK
Cable Rewinding on Drum | Weight of Cable | 1850 kg (drum + cable) – matches packing list
Cable Rewinding on Drum | Drum Length Verification | 250 mtr – verified
Packing & Marking | Cable End Sealing | OK
Packing & Marking | Drum Stencilling & Marking | Stencil clear on both flanges – OK |  | Stencil complete: size, length, PO, drum no., rotation arrow.
Inprocess Record Verification | Wire Drawing | Records complete for offered batch – OK
Inprocess Record Verification | Core Insulation | Ok |  | Thickness & spark test logs complete.
Inprocess Record Verification | Core Laying | Core laying & filler arrangement as per drawing – OK
Inprocess Record Verification | Inner Sheathing | Verified – OK
Inprocess Record Verification | Armouring | Strand count & coverage logged – OK
Inprocess Record Verification | Outersheathing | Thickness & printing logged – OK
Raw Material / Bought out Items TC Verification | Al Wire Rod | Ok |  | Conductivity / composition within limit – OK.
Raw Material / Bought out Items TC Verification | PVC Compound | Ok
Raw Material / Bought out Items TC Verification | HDPE Compound | TC verified – grade & batch match – OK
Raw Material / Bought out Items TC Verification | Armour GI | GI armour TC verified – Zn coating OK
Raw Material / Bought out Items TC Verification | Water Swellable Tape / Yard | OK
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Ok |  | No unsafe condition during walk-through.
Other Compliances for Manufacturing Facility | House Keeping | Ok
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Ok |  | Megger / HV / gauge cal certificates valid.
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Ok |  | No adverse social-compliance observation.

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | Major
Default | 2 | Critical

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Ok |  | Test results satisfactory for offered lot.
Inspection Summary | Technical Clearance | Subject to rectification of minor defects |  | Subject to rectification or not cleared for dispatch.
Inspection Summary | Declaration | I hereby declare that the above LT Power Cable lot has been inspected in the presence of the vendor representative and found satisfactory as per the approved QAP / IS standard, and is cleared for dispatch. |  | Lot cleared wording consistent with test outcome.