## Checklist Details
Title | Details
Checklist name | LT_Power_Cables
Category | LT
Subcategory | Power Cables
Description
Site | IIM Ahmedabad
Started by | Dhruvit
Started On | Aug 12, 2026, 02:46 PM
Status | Completed
Location | 0,0
Completed by | Dhruvit
Completed on | Aug 12, 2026, 02:46 PM
Created by | Dhruvit
Created on | Aug 12, 2026, 11:13 AM

## Basic Details
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Basic Details | SAP Code | 10571550
Basic Details | Cable Size | 1C x 630 sq.mm Al, XLPE, Unarmoured
Basic Details | Vendor Name | Polycab India Ltd.
Basic Details | Offered Qty | 5 Drums / 2500 mtr
Basic Details | PO Details | PO No. 4500152345 dated 12-Jun-2026
Basic Details | Batch Nos | HV/LT/CAB/260715/01 to HV/LT/CAB/260715/06
Basic Details | AEML Engineer & Designation | Priya Nair, Executive Engineer (Inspection)
Basic Details | Vendor Engineer & Designation | Ramesh Pillai, Works Manager
Basic Details | Date of Inspection | Aug 12, 2026

## Characteristics _ Parameter
Section | Title | Input | Measurement | Notes | Images | Videos | Documents
Physical Checks | Overall Cable Dia | 41.8 mm (as per GA / QAP)
Physical Checks | Ovality of Cable | 2.0% – at limit, accepted
Physical Checks | Outer Sheath Thickness | Avg 2.65 mm, Min 2.50 mm – OK
Physical Checks | Water Swellable Tape thickness | 0.25 mm – as per BOM |  | Water swellable tape continuous under sheath – OK.
Physical Checks | Armour Strand Size | 2.5 mm dia GI wire
Physical Checks | No of Armour Strands | 56 Nos
Physical Checks | Diameter over Armour | 45.0 mm
Physical Checks | Diameter over Inner Sheath | 38.2 mm
Physical Checks | Thickness of Inner Sheath | Avg 1.30 mm, Min 1.10 mm – OK
Physical Checks | Diameter over laid up | 35.0 mm
Physical Checks | Insulation Thickness | 1.85 mm – conforms to IS 7098
Physical Checks | No of Strands in conductor | 37 strands of 3.15 mm dia
Physical Checks | shape of conductor | Sector shaped
Physical Checks | Filler Diameter | 4.5 mm – as per construction
Physical Checks | Verification of Water Blocking construction in conductor | Water blocking yarns present between strand layers – OK
Acceptance Tests | Conductor Resistance Tests | Measured values within IS / approved limit – Pass |  | Corrected to 20°C; all phases within max Ω/km.
Acceptance Tests | High Voltage test @3kV for 5 minutes in all cores | No failure observed during 5 min withstand – Pass |  | HV kit cal valid; test witnessed – Pass.
Acceptance Tests | IR Test | IR phase–earth 80 MΩ – below acceptance; retest pending |  | IR below acceptance on phase–earth.
Acceptance Tests | Hot Set Test on Insulation | Within IS 7098 limits – Pass |  | Lab result attached with report – Pass.
Acceptance Tests | Tensile Strength and Elongation for Insulation & Sheath | Sheath elongation after ageing below min – fail
Acceptance Tests | Water Swellable Tape Swell height | 7.5 mm swell – within limit – Pass
Acceptance Tests | Armour Tests - Mass of Zinc Coating & Uniformity of Zinc coating | Pass – TC from armour sub-vendor reviewed
Acceptance Tests | Tests on HDPE Outer Sheath -1. Density 2.Thickness 3. Shrinkage 4. Pressure test at high temperature 5. Tensile Strength Without ageing & After ageing 6. Elongation at break 7. Without ageing & After ageing | Density, thickness, shrinkage, pressure, TS & elongation – all Pass
Acceptance Tests | Water Penetration Test | No water penetration beyond sealed length – Pass
Acceptance Tests | Anti Termite & Anti Rodent check | Additive present as declared; marking OK – Pass
Acceptance Tests | FRLS Outer Sheath -Flammability Test | Flammability test Pass as per IEC / IS |  | Flame did not propagate beyond mark – Pass.
Acceptance Tests | FRLS Outer Sheath-Oxygen Index Test | OI 27% – below min 30%; oxygen index fail |  | Compound OI out of FRLS band.
Acceptance Tests | FRLS Outer Sheath -Temperature Index | Temperature index OK – Pass |  | TI as per FRLS compound TC – Pass.
Acceptance Tests | FRLS Outersheath -Halogen Gas Acid Evaluation | Pass – low halogen as required
Acceptance Tests | FRLS Outer Sheath-Smoke Density | Max smoke density < specified – Pass |  | Smoke density rating within max – Pass.
Cable Rewinding on Drum | Cable Appearances / Damages check | Deep sheath cut / abrasion on outer layer – damage; rework pending
Cable Rewinding on Drum | Outer sheath colour | Black outer sheath – OK
Cable Rewinding on Drum | Printing & Embossing | Printing clear: size, voltage grade, IS mark, manufacturer, year – OK
Cable Rewinding on Drum | Sequential Length Marking | Length marking accurate within tolerance – OK |  | Sequential marking accuracy within tolerance.
Cable Rewinding on Drum | MS Plates & Spinndle | OK
Cable Rewinding on Drum | Weight of Cable | 2100 kg gross – OK
Cable Rewinding on Drum | Drum Length Verification | 500 mtr ±0.5% – OK
Packing & Marking | Cable End Sealing | Sealing intact – OK |  | Both ends heat-shrink capped – OK.
Packing & Marking | Drum Stencilling & Marking | OK |  | Marking as per IS / AEML packing spec.
Inprocess Record Verification | Wire Drawing | Wire drawing QC sheets reviewed – OK
Inprocess Record Verification | Core Insulation | Ok
Inprocess Record Verification | Core Laying | Verified – OK
Inprocess Record Verification | Inner Sheathing | In-process OK
Inprocess Record Verification | Armouring | In-process OK
Inprocess Record Verification | Outersheathing | OK
Raw Material / Bought out Items TC Verification | Al Wire Rod | Ok
Raw Material / Bought out Items TC Verification | PVC Compound | Ok
Raw Material / Bought out Items TC Verification | HDPE Compound | TC verified – grade & batch match – OK
Raw Material / Bought out Items TC Verification | Armour GI | GI armour TC verified – Zn coating OK
Raw Material / Bought out Items TC Verification | Water Swellable Tape / Yard | Water swellable tape TC OK
Other Compliances for Manufacturing Facility | Safety Aspects in Facility | Ok |  | No unsafe condition during walk-through.
Other Compliances for Manufacturing Facility | House Keeping | Ok
Other Compliances for Manufacturing Facility | Eco-friendly Waste Segregation, Collection and Storage Practices w.r.t Hazardous / Non-Hazardous Materials | Ok
Other Compliances for Manufacturing Facility | Calibration of Testing Instruments | Ok
Other Compliances for Manufacturing Facility | SA 8000 Compliance | Not Ok

## Inspection Observations
Section | Observations | Answer | Measurement | Notes | Images | Videos | Documents
Default | 1. | Major
Default | 2 | Minor |  | No blocking issue on observation point 2.

## Inspection Conclusion
Section | Title | Answer | Measurement | Notes | Images | Videos | Documents
Inspection Summary | Test Results | Ok
Inspection Summary | Technical Clearance | Yes
Inspection Summary | Declaration | Inspection completed jointly with vendor QA. Observations of Minor severity noted above shall be closed before final dispatch where applicable.